`

September 5, 2018

Mr. Dan Winkler

Phoenix Park

Phone: 321.302.1047

119 Signature Drive

Melbourne Beach, Fl 32951

email: danphoenixpark@gmail.com

Re:               Harbor Island Beach Club

Brevard County, Florida

Ingenuity Engineers Project No. I18354.00

Subject:	Preliminary Electrical Load Summary and Conductor Laterals for

FPL Preliminary coordination

Dear Mr. Winkler:

The following is a basic project summary and the preliminary electrical load summary and conductor laterals for the above referenced new residential building project.

The overall project will consist of (54) single family homes and 89 condominium units constructed within (3) building types (Building types A, B, C are the same and types E and F and unique. There will also be a boat dock with 42 powered boat slips.

Residential Single Family load Summary-120/240V single phase

The single family homes will be served at 120/240v single phase and will require pad mounted utility transformers to be located within the residential street scape.

54 residences @ 13kva (demand) each = 702Kva

Condominium Building types A, B and C-120/208v three phase

We will be requesting a single pad mounted utility grade transformer at a secondary voltage of 120/208v 3 phase 4 wire for each of the (3) buildings located directly adjacent to each building.

Building A, B, C, House Loading

House and Parking Garage Ltg/ Recepts.       =   15 kva

Elevators (1) @ 40 hp                                     =   40 kva

Irrigation Pumps (1) @10 hp                            =   10 kva

Garage Ventilation (1) @5hp                            =    5 kva

Total House Load            = 70kva or 194 amps

--- 200 amp service entrance.

This service will provide house power to the common areas of the

building.

The service will be metered via a direct meter system.

Feeder shall be (1) sets of (4) # 300Kcmil Al.

Condo Building A, B, C, Loading

16 condo units at 31kva each x .39 Demand = 194 kva or 539 amps

--- Use 600 amp service entrance main.

This service will serve residential apartments via a modular meter

center.

Feeder shall be (2) sets of (4) # 500Kcmil Al.

Building A, B, C, totals = 264Kva or 733 amps for each building

Condominium Building types D-120/208v three phase

We will be requesting a single pad mounted utility grade transformer at a secondary voltage of 120/208v 3 phase 4 wire for each building located directly adjacent to the building.

Building D House Loading

House and Parking Garage Ltg/ Recepts.       =   15 kva

Elevators (1) @ 40 hp                                     =   40 kva

Irrigation Pumps (1) @10 hp                            =   10 kva

Sewage lift station (2) pumps at 20 hp             =    45Kva

Total House Load             =   110Kva or 305 amps

--- 400 amp service entrance.

This service will provide house power to the common areas of the

Buildings as well as the sewage lift station.

The service will be metered via a direct meter system.

Feeder shall be (2) sets of (4) # 300Kcmil Al)

Condo Building D Loading

17 Condo units at 31kva each x .39 Demand = 206kva or 571 amps

--- Use 600 amp service entrance main.

This service will serve residential apartments via a modular meter

center.

Feeder shall be (2) sets of (4) # 500Kcmil Al.

Building D totals = 271Kva or 752 amps

Condominium Building types E-120/208v three phase

We will be requesting a single pad mounted utility grade transformer at a secondary voltage of 120/208v 3 phase 4 wire for each building located directly adjacent to the building.

Building E House Loading

House and Parking Garage Ltg/ Recepts.       =   20 kva

Elevators (1) @ 40 hp                                     =   40 kva

Irrigation Pumps (1) @10 hp                            =   10 kva

Amenity areas                                                 =    70 kva

Total House Load             = 140 Kva or 389 amps

--- 400 amp service entrance.

This service will provide power to the common areas and amenity

areas of the building.

The service will be metered via a direct meter system.

Feeder shall be (2) sets of (4) # 300Kcmil Al)

Condo Building E Loading

24 Condo units at 31kva each x .35 Demand = 261kva or 723 amps

--- Use 800 amp service entrance main.

This service will serve residential apartments via a modular meter

center.

Feeder shall be (2) sets of (4) # 750Kcmil Al.

Building E totals = 401Kva or 1113 amps

Boat Dock Electrical Service -120/208V Three phase

The boat dock will be served at 120/208v three phase and will require a pad mounted utility transformer to be located within the boat dock service entrance.

42 slips @ 4Kva per slip (demand)   = 168Kva

--- Use 600 amp service entrance main.

This service will serve the boat dock system via a CT meter system

Feeder shall be (2) sets of (4) # 500Kcmil Al.

Totals

Single Family Residence =    702 Kva Single Phase

Boat Dock system           =    168 Kva Three Phase

Condo Buildings              = 1,509 Kva Three Phase

Total                               = 2,379Kva

If you have any additional questions or comments please contact me at any time.

Sincerely,

David F. Green, Jr.

President/CEO